## Sheet1
MasterID29 | SlaveID30 | InUse | IsPreDefined | IOConnection | Description | PointType | WireNumber | OrderByPoint | CableName | DeviceName | ActualDeviceName | DeviceManufacturer | DeviceCost | System | AssocMaster | MasterType | SlaveType | ControllerName | Comments31
1 | 2 | TRUE | FALSE | X1 | FAN STATUS | DI | 2X1 | 0 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-AHU-B-4-1 | 01-01 | Xenta 401 | Xenta 411 | O_MSSB_B1
1 | 2 | TRUE | FALSE | X2 | FAN STATUS | DI | 2X2 | 1 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-AHU-B-4-2 | 01-01 | Xenta 401 | Xenta 411 | O_MSSB_B1
1 | 2 | TRUE | FALSE | X3 | FAN STATUS | DI | 2X3 | 2 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-AHU-B-4-3 | 01-01 | Xenta 401 | Xenta 411 | O_MSSB_B1
1 | 2 | TRUE | FALSE | X4 | FAN STATUS | DI | 2X4 | 3 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-AHU-B-5-1 | 01-01 | Xenta 401 | Xenta 411 | O_MSSB_B1
1 | 2 | TRUE | FALSE | X5 | FAN STATUS | DI | 2X5 | 4 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-GEF-B1 | 01-01 | Xenta 401 | Xenta 411 | O_MSSB_B1
1 | 2 | FALSE | FALSE | X6 |  |  |  | 5 | [6 empty] | 01-01 | Xenta 401 | Xenta 411 | O_MSSB_B1
1 | 2 | TRUE | FALSE | X7 | AC PB | DI | 2X7 | 6 | 1Pair 7/0.2 Screen | Series 2000- | P/Button | CLIPSAL | 0 | O-AHU-B-4-1 | 01-01 | Xenta 401 | Xenta 411 | O_MSSB_B1
1 | 2 | FALSE | FALSE | X8 |  |  |  | 7 | [6 empty] | 01-01 | Xenta 401 | Xenta 411 | O_MSSB_B1
1 | 2 | TRUE | FALSE | X9 | AC PB | DI | 2X9 | 8 | 1Pair 7/0.2 Screen | Series 2000- | P/Button | CLIPSAL | 0 | O-AHU-B-4-2 | 01-01 | Xenta 401 | Xenta 411 | O_MSSB_B1
1 | 2 | FALSE | FALSE | X10 |  |  |  | 9 | [6 empty] | 01-01 | Xenta 401 | Xenta 411 | O_MSSB_B1
1 | 3 | TRUE | FALSE | K1 | FAN ENABLE | DO | 3K1 | 0 | Building Wire | MSSB | Interface Relay | _ | 0 | O-AHU-B-4-1 | 01-02 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 3 | TRUE | FALSE | K2 | FAN ENABLE | DO | 3K2 | 1 | Building Wire | MSSB | Interface Relay | _ | 0 | O-AHU-B-4-2 | 01-02 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 3 | TRUE | FALSE | K3 | FAN ENABLE | DO | 3K3 | 2 | Building Wire | MSSB | Interface Relay | _ | 0 | O-AHU-B-4-3 | 01-02 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 3 | TRUE | FALSE | K4 | FAN ENABLE | DO | 3K4 | 3 | Building Wire | MSSB | Interface Relay | _ | 0 | O-AHU-B-5-1 | 01-02 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 3 | TRUE | FALSE | K5 | FAN ENABLE | DO | 3K5 | 4 | Building Wire | MSSB | Interface Relay | _ | 0 | O-GEF-B1 | 01-02 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 3 | TRUE | FALSE | U1 | AC PB | DI | 3U1 | 5 | 1Pair 7/0.2 Screen | Series 2000- | P/Button | CLIPSAL | 0 | O-AHU-B-4-3 | 01-02 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 3 | FALSE | FALSE | U2 |  |  |  | 6 | [6 empty] | 01-02 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 3 | FALSE | FALSE | U3 |  |  |  | 7 | [6 empty] | 01-02 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 3 | TRUE | FALSE | U4 | AC PB | DI | 3U4 | 8 | 1Pair 7/0.2 Screen | Series 2000- | P/Button | CLIPSAL | 0 | O-AHU-B-5-1 | 01-02 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 4 | FALSE | FALSE | K1 |  |  |  | 0 | [6 empty] | 01-03 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 4 | TRUE | FALSE | K2 | RUN NEON | DO | 4K2 | 1 | Building Wire | 24 vac | Neon Indicator | Clipsal | 0 | O-AHU-B-4-1 | 01-03 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 4 | FALSE | FALSE | K3 |  |  |  | 2 | [6 empty] | 01-03 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 4 | TRUE | FALSE | K4 | RUN NEON | DO | 4K4 | 3 | Building Wire | 24 vac | Neon Indicator | Clipsal | 0 | O-AHU-B-4-2 | 01-03 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 4 | TRUE | FALSE | K5 | RUN NEON | DO | 4K5 | 4 | Building Wire | 24 vac | Neon Indicator | Clipsal | 0 | O-AHU-B-4-3 | 01-03 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 4 | FALSE | FALSE | U1 |  |  |  | 5 | [6 empty] | 01-03 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 4 | TRUE | FALSE | U2 | SUPPLY AIR TEMP | TI | 4U2 | 6 | 1Pair 7/0.2 Screen | AVG TE705-B-21-B-1 | Duct Average Temp | MAMAC | 71.25 | O-AHU-B-4-1 | 01-03 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 4 | TRUE | FALSE | U3 | SUPPLY AIR TEMP | TI | 4U3 | 7 | 1Pair 7/0.2 Screen | AVG TE705-B-21-B-1 | Duct Average Temp | MAMAC | 71.25 | O-AHU-B-4-3 | 01-03 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 4 | TRUE | FALSE | U4 | SUPPLY AIR TEMP | TI | 4U4 | 8 | 1Pair 7/0.2 Screen | AVG TE705-B-21-B-1 | Duct Average Temp | MAMAC | 71.25 | O-AHU-B-5-1 | 01-03 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 5 | FALSE | FALSE | K1 |  |  |  | 0 | [6 empty] | 01-04 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 5 | TRUE | FALSE | K2 | RUN NEON | DO | 5K2 | 1 | Building Wire | 24 vac | Neon Indicator | Clipsal | 0 | O-AHU-B-5-1 | 01-04 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 5 | FALSE | FALSE | K3 |  |  |  | 2 | [6 empty] | 01-04 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 5 | FALSE | FALSE | K4 |  |  |  | 3 | [6 empty] | 01-04 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 5 | TRUE | FALSE | K5 | EDH 1 | DO | 5K5 | 4 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-4-1.ZA | 01-04 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 5 | TRUE | FALSE | U1 | ZONE TEMP | TI | 5U1 | 5 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-4-1.ZA | 01-04 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 5 | TRUE | FALSE | U2 | ZONE TEMP | TI | 5U2 | 6 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-4-1.ZB | 01-04 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 5 | TRUE | FALSE | U3 | ZONE TEMP | TI | 5U3 | 7 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-4-2 | 01-04 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 5 | FALSE | FALSE | U4 |  |  |  | 8 | [6 empty] | 01-04 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 6 | TRUE | FALSE | K1 | EDH 1 | DO | 6K1 | 0 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-4-1.ZB | 01-05 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 6 | TRUE | FALSE | K2 | EDH 1 | DO | 6K2 | 1 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-4-2 | 01-05 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 6 | TRUE | FALSE | K3 | EDH 2 | DO | 6K3 | 2 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-4-2 | 01-05 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 6 | TRUE | FALSE | K4 | EDH 1 | DO | 6K4 | 3 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-4-3.ZA | 01-05 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 6 | TRUE | FALSE | K5 | EDH 1 | DO | 6K5 | 4 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-4-3.ZB | 01-05 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 6 | TRUE | FALSE | U1 | ZONE TEMP | TI | 6U1 | 5 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-4-3.ZA | 01-05 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 6 | TRUE | FALSE | U2 | ZONE TEMP | TI | 6U2 | 6 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-4-3.ZB | 01-05 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 6 | FALSE | FALSE | U3 |  |  |  | 7 | [6 empty] | 01-05 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 6 | FALSE | FALSE | U4 |  |  |  | 8 | [6 empty] | 01-05 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 7 | TRUE | FALSE | K1 | EDH 1 | DO | 7K1 | 0 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-5-1.ZA | 01-06 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 7 | TRUE | FALSE | K2 | EDH 1 | DO | 7K2 | 1 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-5-1.ZB | 01-06 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 7 | TRUE | FALSE | K3 | EDH 2 | DO | 7K3 | 2 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-5-1.ZB | 01-06 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 7 | TRUE | FALSE | K4 | EDH 3 | DO | 7K4 | 3 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-5-1.ZB | 01-06 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 7 | TRUE | FALSE | K5 | EDH 1 | DO | 7K5 | 4 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-5-1.ZC | 01-06 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 7 | TRUE | FALSE | U1 | ZONE TEMP | TI | 7U1 | 5 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-5-1.ZA | 01-06 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 7 | TRUE | FALSE | U2 | ZONE TEMP | TI | 7U2 | 6 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-5-1.ZB | 01-06 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 7 | TRUE | FALSE | U3 | ZONE TEMP | TI | 7U3 | 7 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-5-1.ZC | 01-06 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 7 | FALSE | FALSE | U4 |  |  |  | 8 | [6 empty] | 01-06 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 8 | FALSE | FALSE | K1 |  |  |  | 0 | [6 empty] | 01-07 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 8 | FALSE | FALSE | K2 |  |  |  | 1 | [6 empty] | 01-07 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 8 | FALSE | FALSE | K3 |  |  |  | 2 | [6 empty] | 01-07 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 8 | TRUE | FALSE | K4 | COOLING CALL TO INET | DO | 8K4 | 3 | Building Wire | [5 empty] | 01-07 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 8 | FALSE | FALSE | K5 |  |  |  | 4 | [6 empty] | 01-07 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 8 | TRUE | FALSE | U1 | RA TEMP | TI | 8U1 | 5 | 1Pair 7/0.2 Screen | STD100-200 | Duct Temperature | TAC | 18 | O-AHU-B-4-1 | 01-07 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 8 | TRUE | FALSE | U2 | RA HUMIDITY | AI | 8U2 | 6 | 3 Core 14/0.20 Screen | SHD100 | Duct Humidity Sensor | TAC | 179 | O-AHU-B-4-1 | 01-07 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 8 | FALSE | FALSE | U3 |  |  |  | 7 | [6 empty] | 01-07 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 8 | FALSE | FALSE | U4 |  |  |  | 8 | [6 empty] | 01-07 | Xenta 401 | Xenta 421A | O_MSSB_B1
1 | 9 | TRUE | FALSE | Y1 | CHWV | AO | 9Y1 | 0 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-4-1 | 01-08 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 9 | TRUE | FALSE | Y2 | CHWV | AO | 9Y2 | 1 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-4-2 | 01-08 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 9 | TRUE | FALSE | Y3 | CHWV | AO | 9Y3 | 2 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-4-3 | 01-08 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 9 | TRUE | FALSE | Y4 | CHWV | AO | 9Y4 | 3 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-5-1 | 01-08 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 9 | FALSE | FALSE | Y5 |  |  |  | 4 | [6 empty] | 01-08 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 9 | FALSE | FALSE | Y6 |  |  |  | 5 | [6 empty] | 01-08 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 9 | FALSE | FALSE | Y7 |  |  |  | 6 | [6 empty] | 01-08 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 9 | FALSE | FALSE | Y8 |  |  |  | 7 | [6 empty] | 01-08 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 10 | TRUE | FALSE | Y1 | F&B DAMPER | AO | 10Y1 | 0 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-4-1.ZA | 01-09 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 10 | FALSE | FALSE | Y2 |  |  |  | 1 | [6 empty] | 01-09 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 10 | TRUE | FALSE | Y3 | F&B DAMPER | AO | 10Y3 | 2 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-4-1.ZB | 01-09 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 10 | FALSE | FALSE | Y4 |  |  |  | 3 | [6 empty] | 01-09 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 10 | TRUE | FALSE | Y5 | F&B DAMPER | AO | 10Y5 | 4 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-4-3.ZA | 01-09 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 10 | FALSE | FALSE | Y6 |  |  |  | 5 | [6 empty] | 01-09 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 10 | TRUE | FALSE | Y7 | F&B DAMPER | AO | 10Y7 | 6 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-4-3.ZB | 01-09 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 10 | FALSE | FALSE | Y8 |  |  |  | 7 | [6 empty] | 01-09 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 11 | TRUE | FALSE | Y1 | F&B DAMPER | AO | 11Y1 | 0 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-5-1.ZA | 01-10 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 11 | FALSE | FALSE | Y2 |  |  |  | 1 | [6 empty] | 01-10 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 11 | TRUE | FALSE | Y3 | F&B DAMPER | AO | 11Y3 | 2 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-5-1.ZB | 01-10 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 11 | FALSE | FALSE | Y4 |  |  |  | 3 | [6 empty] | 01-10 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 11 | TRUE | FALSE | Y5 | F&B DAMPER | AO | 11Y5 | 4 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-5-1.ZC | 01-10 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 11 | FALSE | FALSE | Y6 |  |  |  | 5 | [6 empty] | 01-10 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 11 | FALSE | FALSE | Y7 |  |  |  | 6 | [6 empty] | 01-10 | Xenta 401 | Xenta 491 | O_MSSB_B1
1 | 11 | FALSE | FALSE | Y8 |  |  |  | 7 | [6 empty] | 01-10 | Xenta 401 | Xenta 491 | O_MSSB_B1
12 | 13 | TRUE | FALSE | K1 | FAN ENABLE | DO | 13K1 | 0 | Building Wire | MSSB | Interface Relay | _ | 0 | O-AHU-B-4-4 | 12-01 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 13 | TRUE | FALSE | K2 | FAN ENABLE | DO | 13K2 | 1 | Building Wire | MSSB | Interface Relay | _ | 0 | O-AHU-B-4-5 | 12-01 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 13 | TRUE | FALSE | K3 | FAN ENABLE | DO | 13K3 | 2 | Building Wire | MSSB | Interface Relay | _ | 0 | O-AHU-B-4-6 | 12-01 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 13 | TRUE | FALSE | K4 | FAN ENABLE | DO | 13K4 | 3 | Building Wire | MSSB | Interface Relay | _ | 0 | O-AHU-B-5-2 | 12-01 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 13 | FALSE | FALSE | K5 |  |  |  | 4 | [6 empty] | 12-01 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 13 | TRUE | FALSE | U1 | FAN STATUS | DI | 13U1 | 5 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-AHU-B-4-4 | 12-01 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 13 | TRUE | FALSE | U2 | FAN STATUS | DI | 13U2 | 6 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-AHU-B-4-5 | 12-01 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 13 | TRUE | FALSE | U3 | FAN STATUS | DI | 13U3 | 7 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-AHU-B-4-6 | 12-01 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 13 | TRUE | FALSE | U4 | FAN STATUS | DI | 13U4 | 8 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-AHU-B-5-2 | 12-01 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 14 | TRUE | FALSE | K1 | RUN NEON | DO | 14K1 | 0 | Building Wire | 24 vac | Neon Indicator | Clipsal | 0 | O-AHU-B-4-4 | 12-02 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 14 | TRUE | FALSE | K2 | RUN NEON | DO | 14K2 | 1 | Building Wire | 24 vac | Neon Indicator | Clipsal | 0 | O-AHU-B-4-5 | 12-02 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 14 | TRUE | FALSE | K3 | RUN NEON | DO | 14K3 | 2 | Building Wire | 24 vac | Neon Indicator | Clipsal | 0 | O-AHU-B-4-6 | 12-02 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 14 | TRUE | FALSE | K4 | RUN NEON | DO | 14K4 | 3 | Building Wire | 24 vac | Neon Indicator | Clipsal | 0 | O-AHU-B-5-2 | 12-02 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 14 | FALSE | FALSE | K5 |  |  |  | 4 | [6 empty] | 12-02 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 14 | TRUE | FALSE | U1 | AC PB | DI | 14U1 | 5 | 1Pair 7/0.2 Screen | Series 2000- | P/Button | CLIPSAL | 0 | O-AHU-B-4-4 | 12-02 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 14 | TRUE | FALSE | U2 | AC PB | DI | 14U2 | 6 | 1Pair 7/0.2 Screen | Series 2000- | P/Button | CLIPSAL | 0 | O-AHU-B-4-5 | 12-02 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 14 | TRUE | FALSE | U3 | AC PB | DI | 14U3 | 7 | 1Pair 7/0.2 Screen | Series 2000- | P/Button | CLIPSAL | 0 | O-AHU-B-4-6 | 12-02 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 14 | TRUE | FALSE | U4 | SUPPLY AIR TEMP | TI | 14U4 | 8 | 1Pair 7/0.2 Screen | AVG TE705-B-21-B-1 | Duct Average Temp | MAMAC | 71.25 | O-AHU-B-5-2 | 12-02 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 15 | FALSE | FALSE | K1 |  |  |  | 0 | [6 empty] | 12-03 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 15 | FALSE | FALSE | K2 |  |  |  | 1 | [6 empty] | 12-03 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 15 | TRUE | FALSE | K3 | EDH 1 | DO | 15K3 | 2 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-4-4 | 12-03 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 15 | TRUE | FALSE | K4 | EDH 1 | DO | 15K4 | 3 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-4-5 | 12-03 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 15 | TRUE | FALSE | K5 | EDH 1 | DO | 15K5 | 4 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-4-6 | 12-03 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 15 | TRUE | FALSE | U1 | AC PB | DI | 15U1 | 5 | 1Pair 7/0.2 Screen | Series 2000- | P/Button | CLIPSAL | 0 | O-AHU-B-5-2 | 12-03 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 15 | TRUE | FALSE | U2 | FAN STATUS | DI | 15U2 | 6 | 1Pair 7/0.20 Screen | VFC by others | Volt free contact | _ | 0 | O-AHU-B423 | 12-03 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 15 | TRUE | FALSE | U3 | SUPPLY AIR TEMP | AI | 15U3 | 7 | 1Pair 7/0.20 Screen | STD-100 150 | Duct Temperature | TAC | 0 | O-AHU-B423 | 12-03 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 15 | TRUE | FALSE | U4 | ZONE TEMP | AI | 15U4 | 8 | 1Pair 7/0.20 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B423 | 12-03 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 16 | TRUE | FALSE | K1 | EDH 1 | DO | 16K1 | 0 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-5-2.A | 12-04 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 16 | TRUE | FALSE | K2 | EDH 1 | DO | 16K2 | 1 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-5-2.B | 12-04 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 16 | TRUE | FALSE | K3 | EDH 1 | DO | 16K3 | 2 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-5-2.C | 12-04 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 16 | TRUE | FALSE | K4 | EDH 1 | DO | 16K4 | 3 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-5-2.D | 12-04 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 16 | TRUE | FALSE | K5 | COOLING CALL TO INET | DO | 16K5 | 4 | Building Wire | [5 empty] | 12-04 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 16 | TRUE | FALSE | U1 | ZONE TEMP | TI | 16U1 | 5 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-4-4 | 12-04 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 16 | TRUE | FALSE | U2 | ZONE TEMP | TI | 16U2 | 6 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-4-5 | 12-04 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 16 | TRUE | FALSE | U3 | ZONE TEMP | TI | 16U3 | 7 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-4-6 | 12-04 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 16 | FALSE | FALSE | U4 |  |  |  | 8 | [6 empty] | 12-04 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 17 | FALSE | FALSE | K1 |  |  |  | 0 | [6 empty] | 12-05 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 17 | FALSE | FALSE | K2 |  |  |  | 1 | [6 empty] | 12-05 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 17 | FALSE | FALSE | K3 |  |  |  | 2 | [6 empty] | 12-05 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 17 | FALSE | FALSE | K4 |  |  |  | 3 | [6 empty] | 12-05 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 17 | FALSE | FALSE | K5 |  |  |  | 4 | [6 empty] | 12-05 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 17 | TRUE | FALSE | U1 | ZONE TEMP | TI | 17U1 | 5 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-5-2.A | 12-05 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 17 | TRUE | FALSE | U2 | ZONE TEMP | TI | 17U2 | 6 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-5-2.B | 12-05 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 17 | TRUE | FALSE | U3 | ZONE TEMP | TI | 17U3 | 7 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-5-2.C | 12-05 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 17 | TRUE | FALSE | U4 | ZONE TEMP | TI | 17U4 | 8 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-5-2.D | 12-05 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 18 | TRUE | FALSE | Y1 | CHWV | AO | 18Y1 | 0 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-4-4 | 12-06 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 18 | TRUE | FALSE | Y2 | CHWV | AO | 18Y2 | 1 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-4-5 | 12-06 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 18 | TRUE | FALSE | Y3 | CHWV | AO | 18Y3 | 2 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-4-6 | 12-06 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 18 | TRUE | FALSE | Y4 | CHWV | AO | 18Y4 | 3 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-5-2 | 12-06 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 18 | TRUE | FALSE | Y5 | CHWV | AO | 18Y5 | 4 | 4Core 14/0.20 | MZ18A(mod) | Valve Actuator | TAC | 113 | O-AHU-B423 | 12-06 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 18 | TRUE | FALSE | Y6 | EDH SCR | AO | 18Y6 | 5 | 4Core 14/0.20 | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B423 | 12-06 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 18 | FALSE | FALSE | Y7 |  |  |  | 6 | [6 empty] | 12-06 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 18 | FALSE | FALSE | Y8 |  |  |  | 7 | [6 empty] | 12-06 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 19 | TRUE | FALSE | Y1 | F&B DAMPER | AO | 19Y1 | 0 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-5-2.A | 12-07 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 19 | FALSE | FALSE | Y2 |  |  |  | 1 | [6 empty] | 12-07 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 19 | TRUE | FALSE | Y3 | F&B DAMPER | AO | 19Y3 | 2 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-5-2.B | 12-07 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 19 | FALSE | FALSE | Y4 |  |  |  | 3 | [6 empty] | 12-07 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 19 | TRUE | FALSE | Y5 | F&B DAMPER | AO | 19Y5 | 4 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-5-2.C | 12-07 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 19 | FALSE | FALSE | Y6 |  |  |  | 5 | [6 empty] | 12-07 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 19 | TRUE | FALSE | Y7 | F&B DAMPER | AO | 19Y7 | 6 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-5-2.D | 12-07 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 19 | FALSE | FALSE | Y8 |  |  |  | 7 | [6 empty] | 12-07 | Xenta 401 | Xenta 491 | O_MSSB_B2
20 | 21 | TRUE | FALSE | K1 | FAN ENABLE | DO | 21K1 | 0 | Building Wire | MSSB | Interface Relay | _ | 0 | O-AHU-B-6-1 | 20-01 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 21 | TRUE | FALSE | K2 | FAN ENABLE | DO | 21K2 | 1 | Building Wire | MSSB | Interface Relay | _ | 0 | O-TEF-B-6-1 | 20-01 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 21 | TRUE | FALSE | K3 | FAN ENABLE | DO | 21K3 | 2 | Building Wire | MSSB | Interface Relay | _ | 0 | O-EF-B-6-2 | 20-01 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 21 | TRUE | FALSE | K4 | FAN ENABLE | DO | 21K4 | 3 | Building Wire | MSSB | Interface Relay | _ | 0 | O-EF-STERILIZER B3 | 20-01 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 21 | FALSE | FALSE | K5 |  |  |  | 4 | [6 empty] | 20-01 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 21 | TRUE | FALSE | U1 | FAN STATUS | DI | 21U1 | 5 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-AHU-B-6-1 | 20-01 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 21 | TRUE | FALSE | U2 | FAN STATUS | DI | 21U2 | 6 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-TEF-B-6-1 | 20-01 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 21 | TRUE | FALSE | U3 | FAN STATUS | DI | 21U3 | 7 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-EF-B-6-2 | 20-01 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 21 | TRUE | FALSE | U4 | FAN STATUS | DI | 21U4 | 8 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-EF-STERILIZER B3 | 20-01 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 22 | TRUE | FALSE | K1 | RUN NEON | DO | 22K1 | 0 | Building Wire | 24 vac | Neon Indicator | Clipsal | 0 | O-AHU-B-6-1.ZA_ZC | 20-02 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 22 | TRUE | FALSE | K2 | RUN NEON | DO | 22K2 | 1 | Building Wire | 24 vac | Neon Indicator | Clipsal | 0 | O-AHU-B-6-1.ZB | 20-02 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 22 | FALSE | FALSE | K3 |  |  |  | 2 | [6 empty] | 20-02 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 22 | TRUE | FALSE | K4 | EDH 1 | DO | 22K4 | 3 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-6-1.ZA | 20-02 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 22 | TRUE | FALSE | K5 | EDH 2 | DO | 22K5 | 4 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-6-1.ZA | 20-02 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 22 | TRUE | FALSE | U1 | AC PB | DI | 22U1 | 5 | 1Pair 7/0.2 Screen | Series 2000- | P/Button | CLIPSAL | 0 | O-AHU-B-6-1.ZA_ZC | 20-02 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 22 | TRUE | FALSE | U2 | AC PB | DI | 22U2 | 6 | [5 empty] | O-AHU-B-6-1.ZB | 20-02 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 22 | FALSE | FALSE | U3 |  |  |  | 7 | [6 empty] | 20-02 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 22 | TRUE | FALSE | U4 | SUPPLY AIR TEMP | TI | 22U4 | 8 | 1Pair 7/0.2 Screen | AVG TE705-B-21-B-1 | Duct Average Temp | MAMAC | 71.25 | O-AHU-B-6-1 | 20-02 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 23 | TRUE | FALSE | K1 | EDH 1 | DO | 23K1 | 0 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-6-1.ZB | 20-03 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 23 | TRUE | FALSE | K2 | EDH 2 | DO | 23K2 | 1 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-6-1.ZB | 20-03 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 23 | TRUE | FALSE | K3 | EDH 1 | DO | 23K3 | 2 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-6-1.ZC | 20-03 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 23 | TRUE | FALSE | K4 | EDH 2 | DO | 23K4 | 3 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-6-1.ZC | 20-03 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 23 | FALSE | FALSE | K5 |  |  |  | 4 | [6 empty] | 20-03 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 23 | FALSE | FALSE | U1 |  |  |  | 5 | [6 empty] | 20-03 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 23 | TRUE | FALSE | U2 | ZONE TEMP | TI | 23U2 | 6 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-6-1.ZA | 20-03 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 23 | TRUE | FALSE | U3 | ZONE TEMP | TI | 23U3 | 7 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-6-1.ZB | 20-03 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 23 | TRUE | FALSE | U4 | ZONE TEMP | TI | 23U4 | 8 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-6-1.ZC | 20-03 | Xenta 401 | Xenta 421A | O_MSSB_B3
20 | 24 | TRUE | FALSE | Y1 | CHWV | AO | 24Y1 | 0 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-6-1 | 20-04 | Xenta 401 | Xenta 491 | O_MSSB_B3
20 | 24 | FALSE | FALSE | Y2 |  |  |  | 1 | [6 empty] | 20-04 | Xenta 401 | Xenta 491 | O_MSSB_B3
20 | 24 | TRUE | FALSE | Y3 | F&B DAMPER | AO | 24Y3 | 2 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-6-1.ZA | 20-04 | Xenta 401 | Xenta 491 | O_MSSB_B3
20 | 24 | FALSE | FALSE | Y4 |  |  |  | 3 | [6 empty] | 20-04 | Xenta 401 | Xenta 491 | O_MSSB_B3
20 | 24 | TRUE | FALSE | Y5 | F&B DAMPER | AO | 24Y5 | 4 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-6-1.ZB | 20-04 | Xenta 401 | Xenta 491 | O_MSSB_B3
20 | 24 | FALSE | FALSE | Y6 |  |  |  | 5 | [6 empty] | 20-04 | Xenta 401 | Xenta 491 | O_MSSB_B3
20 | 24 | TRUE | FALSE | Y7 | F&B DAMPER | AO | 24Y7 | 6 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-6-1.ZC | 20-04 | Xenta 401 | Xenta 491 | O_MSSB_B3
20 | 24 | FALSE | FALSE | Y8 |  |  |  | 7 | [6 empty] | 20-04 | Xenta 401 | Xenta 491 | O_MSSB_B3
25 | 26 | TRUE | FALSE | K1 | FAN ENABLE | DO | 26K1 | 0 | Building Wire | MSSB | Interface Relay | _ | 0 | O-AHU-B-6-2 | 25-01 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 26 | TRUE | FALSE | K2 | FAN ENABLE | DO | 26K2 | 1 | Building Wire | MSSB | Interface Relay | _ | 0 | O-EF PLANT ROOM | 25-01 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 26 | TRUE | FALSE | K3 | FAN ENABLE | DO | 26K3 | 2 | Building Wire | MSSB | Interface Relay | _ | 0 | O-TEF-B-6-3 | 25-01 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 26 | TRUE | FALSE | K4 | FAN ENABLE | DO | 26K4 | 3 | Building Wire | MSSB | Interface Relay | _ | 0 | O-EF-B-6-5 WORKSHOP | 25-01 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 26 | TRUE | FALSE | K5 | FAN ENABLE | DO | 26K5 | 4 | Building Wire | MSSB | Interface Relay | _ | 0 | O-EF-B-6-6 FABRICATION | 25-01 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 26 | TRUE | FALSE | U1 | FAN STATUS | DI | 26U1 | 5 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-AHU-B-6-2 | 25-01 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 26 | TRUE | FALSE | U2 | FAN STATUS | DI | 26U2 | 6 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-EF PLANT ROOM | 25-01 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 26 | TRUE | FALSE | U3 | FAN STATUS | DI | 26U3 | 7 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-TEF-B-6-3 | 25-01 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 26 | TRUE | FALSE | U4 | FAN STATUS | DI | 26U4 | 8 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-EF-B-6-5 WORKSHOP | 25-01 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 27 | TRUE | FALSE | K1 | RUN NEON | DO | 27K1 | 0 | Building Wire | 24 vac | Neon Indicator | Clipsal | 0 | O-AHU-B-6-2 | 25-02 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 27 | FALSE | FALSE | K2 |  |  |  | 1 | [6 empty] | 25-02 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 27 | TRUE | FALSE | K3 | FAN ENABLE | DO | 27K3 | 2 | Building Wire | 24 vac | Neon Indicator | Clipsal | 0 | O-GEF-B-6-5 | 25-02 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 27 | FALSE | FALSE | K4 |  |  |  | 3 | [6 empty] | 25-02 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 27 | TRUE | FALSE | K5 | EDH 1 | DO | 27K5 | 4 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-6-2.ZA | 25-02 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 27 | TRUE | FALSE | U1 | FAN STATUS | DI | 27U1 | 5 | 1Pair 7/0.2 Screen | Pressure switch by others | Pressure Switch |  | 0 | O-EF-B-6-6 FABRICATION | 25-02 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 27 | FALSE | FALSE | U2 |  |  |  | 6 | [6 empty] | 25-02 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 27 | FALSE | FALSE | U3 |  |  |  | 7 | [6 empty] | 25-02 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 27 | FALSE | FALSE | U4 |  |  |  | 8 | [6 empty] | 25-02 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 28 | TRUE | FALSE | K1 | EDH 2 | DO | 28K1 | 0 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-6-2.ZA | 25-03 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 28 | TRUE | FALSE | K2 | EDH 1 | DO | 28K2 | 1 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-6-2.ZB | 25-03 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 28 | TRUE | FALSE | K3 | EDH 1 | DO | 28K3 | 2 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-6-2.ZC | 25-03 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 28 | TRUE | FALSE | K4 | EDH 1 | DO | 28K4 | 3 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-6-2.ZD | 25-03 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 28 | TRUE | FALSE | K5 | EDH 2 | DO | 28K5 | 4 | Building Wire | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B-6-2.ZD | 25-03 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 28 | TRUE | FALSE | U1 | AC PB | DI | 28U1 | 5 | 1Pair 7/0.2 Screen | Series 2000- | P/Button | CLIPSAL | 0 | O-AHU-B-6-2.ZA | 25-03 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 28 | FALSE | FALSE | U2 |  |  |  | 6 | [6 empty] | 25-03 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 28 | TRUE | FALSE | U3 | FAN STATUS | DI | 28U3 | 7 | 1Pair 7/0.2 Screen | Series 2000- | P/Button | CLIPSAL | 0 | O-GEF-B-6-5 | 25-03 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 28 | FALSE | FALSE | U4 |  |  |  | 8 | [6 empty] | 25-03 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 29 | TRUE | FALSE | K1 | LIGHTING ZONE 1 | DO | 29K1 | 0 | Building Wire | MSSB | Interface Relay | _ | 0 | O-LEVEL 4 | 25-04 | Xenta 401 | Xenta 421A | O_MSSB_B4 | Future
25 | 29 | TRUE | FALSE | K2 | LIGHTING ZONE 2 | DO | 29K2 | 1 | Building Wire | MSSB | Interface Relay | _ | 0 | O-LEVEL 4 | 25-04 | Xenta 401 | Xenta 421A | O_MSSB_B4 | Future
25 | 29 | TRUE | FALSE | K3 | LIGHTING ZONE 3 | DO | 29K3 | 2 | Building Wire | MSSB | Interface Relay | _ | 0 | O-LEVEL 4 | 25-04 | Xenta 401 | Xenta 421A | O_MSSB_B4 | Future
25 | 29 | TRUE | FALSE | K4 | LIGHTING ZONE 4 | DO | 29K4 | 3 | Building Wire | MSSB | Interface Relay | _ | 0 | O-LEVEL 4 | 25-04 | Xenta 401 | Xenta 421A | O_MSSB_B4 | Future
25 | 29 | TRUE | FALSE | K5 | COOLING CALL TO INET | DO | 29K5 | 4 | Building Wire | [5 empty] | 25-04 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 29 | FALSE | FALSE | U1 |  |  |  | 5 | [6 empty] | 25-04 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 29 | FALSE | FALSE | U2 |  |  |  | 6 | [6 empty] | 25-04 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 29 | FALSE | FALSE | U3 |  |  |  | 7 | [6 empty] | 25-04 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 29 | FALSE | FALSE | U4 |  |  |  | 8 | [6 empty] | 25-04 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 30 | TRUE | FALSE | K1 | LIGHTING ZONE 1 | DO | 30K1 | 0 | Building Wire | MSSB | Interface Relay | _ | 0 | O-LEVEL 5 | 25-05 | Xenta 401 | Xenta 421A | O_MSSB_B4 | Future
25 | 30 | TRUE | FALSE | K2 | LIGHTING ZONE 2 | DO | 30K2 | 1 | Building Wire | MSSB | Interface Relay | _ | 0 | O-LEVEL 5 | 25-05 | Xenta 401 | Xenta 421A | O_MSSB_B4 | Future
25 | 30 | TRUE | FALSE | K3 | LIGHTING ZONE 3 | DO | 30K3 | 2 | Building Wire | MSSB | Interface Relay | _ | 0 | O-LEVEL 5 | 25-05 | Xenta 401 | Xenta 421A | O_MSSB_B4 | Future
25 | 30 | TRUE | FALSE | K4 | LIGHTING ZONE 4 | DO | 30K4 | 3 | Building Wire | MSSB | Interface Relay | _ | 0 | O-LEVEL 5 | 25-05 | Xenta 401 | Xenta 421A | O_MSSB_B4 | Future
25 | 30 | FALSE | FALSE | K5 |  |  |  | 4 | [6 empty] | 25-05 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 30 | FALSE | FALSE | U1 |  |  |  | 5 | [6 empty] | 25-05 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 30 | FALSE | FALSE | U2 |  |  |  | 6 | [6 empty] | 25-05 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 30 | FALSE | FALSE | U3 |  |  |  | 7 | [6 empty] | 25-05 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 30 | FALSE | FALSE | U4 |  |  |  | 8 | [6 empty] | 25-05 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 31 | TRUE | FALSE | K1 | LIGHTING ZONE 1 | DO | 31K1 | 0 | Building Wire | MSSB | Interface Relay | _ | 0 | O-LEVEL 6 | 25-06 | Xenta 401 | Xenta 421A | O_MSSB_B4 | Future
25 | 31 | TRUE | FALSE | K2 | LIGHTING ZONE 2 | DO | 31K2 | 1 | Building Wire | MSSB | Interface Relay | _ | 0 | O-LEVEL 6 | 25-06 | Xenta 401 | Xenta 421A | O_MSSB_B4 | Future
25 | 31 | TRUE | FALSE | K3 | LIGHTING ZONE 3 | DO | 31K3 | 2 | Building Wire | MSSB | Interface Relay | _ | 0 | O-LEVEL 6 | 25-06 | Xenta 401 | Xenta 421A | O_MSSB_B4 | Future
25 | 31 | TRUE | FALSE | K4 | LIGHTING ZONE 4 | DO | 31K4 | 3 | Building Wire | MSSB | Interface Relay | _ | 0 | O-LEVEL 6 | 25-06 | Xenta 401 | Xenta 421A | O_MSSB_B4 | Future
25 | 31 | FALSE | FALSE | K5 |  |  |  | 4 | [6 empty] | 25-06 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 31 | FALSE | FALSE | U1 |  |  |  | 5 | [6 empty] | 25-06 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 31 | FALSE | FALSE | U2 |  |  |  | 6 | [6 empty] | 25-06 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 31 | FALSE | FALSE | U3 |  |  |  | 7 | [6 empty] | 25-06 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 31 | FALSE | FALSE | U4 |  |  |  | 8 | [6 empty] | 25-06 | Xenta 401 | Xenta 421A | O_MSSB_B4
25 | 32 | TRUE | FALSE | U1 | ZONE TEMP | TI | 32U1 | 0 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-6-2.ZA | 25-07 | Xenta 401 | Xenta 451A | O_MSSB_B4
25 | 32 | TRUE | FALSE | U2 | ZONE TEMP | TI | 32U2 | 1 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-6-2.ZB | 25-07 | Xenta 401 | Xenta 451A | O_MSSB_B4
25 | 32 | TRUE | FALSE | U3 | ZONE TEMP | TI | 32U3 | 2 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-6-2.ZC | 25-07 | Xenta 401 | Xenta 451A | O_MSSB_B4
25 | 32 | TRUE | FALSE | U4 | ZONE TEMP | TI | 32U4 | 3 | 1Pair 7/0.2 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B-6-2.ZD | 25-07 | Xenta 401 | Xenta 451A | O_MSSB_B4
25 | 32 | TRUE | FALSE | U5 | SUPPLY AIR TEMP | TI | 32U5 | 4 | 1Pair 7/0.2 Screen | AVG TE705-B-21-B-1 | Duct Average Temp | MAMAC | 71.25 | O-AHU-B-6-2 | 25-07 | Xenta 401 | Xenta 451A | O_MSSB_B4
25 | 32 | FALSE | FALSE | U6 |  |  |  | 5 | [6 empty] | 25-07 | Xenta 401 | Xenta 451A | O_MSSB_B4
25 | 32 | FALSE | FALSE | U7 |  |  |  | 6 | [6 empty] | 25-07 | Xenta 401 | Xenta 451A | O_MSSB_B4
25 | 32 | FALSE | FALSE | U8 |  |  |  | 7 | [6 empty] | 25-07 | Xenta 401 | Xenta 451A | O_MSSB_B4
25 | 32 | TRUE | FALSE | Y1 | CHWV | AO | 32Y1 | 8 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-6-2 | 25-07 | Xenta 401 | Xenta 451A | O_MSSB_B4
25 | 32 | FALSE | FALSE | Y2 |  |  |  | 9 | [6 empty] | 25-07 | Xenta 401 | Xenta 451A | O_MSSB_B4
25 | 33 | TRUE | FALSE | Y1 | F&B DAMPER | AO | 33Y1 | 0 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-6-2.ZA | 25-08 | Xenta 401 | Xenta 491 | O_MSSB_B4
25 | 33 | FALSE | FALSE | Y2 |  |  |  | 1 | [6 empty] | 25-08 | Xenta 401 | Xenta 491 | O_MSSB_B4
25 | 33 | TRUE | FALSE | Y3 | F&B DAMPER | AO | 33Y3 | 2 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-6-2.ZB | 25-08 | Xenta 401 | Xenta 491 | O_MSSB_B4
25 | 33 | FALSE | FALSE | Y4 |  |  |  | 3 | [6 empty] | 25-08 | Xenta 401 | Xenta 491 | O_MSSB_B4
25 | 33 | TRUE | FALSE | Y5 | F&B DAMPER | AO | 33Y5 | 4 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-6-2.ZC | 25-08 | Xenta 401 | Xenta 491 | O_MSSB_B4
25 | 33 | FALSE | FALSE | Y6 |  |  |  | 5 | [6 empty] | 25-08 | Xenta 401 | Xenta 491 | O_MSSB_B4
25 | 33 | TRUE | FALSE | Y7 | F&B DAMPER | AO | 33Y7 | 6 | 4Core 14/0.20 | Existing Device | Existing Device | _ | 0 | O-AHU-B-6-2.ZD | 25-08 | Xenta 401 | Xenta 491 | O_MSSB_B4
25 | 33 | FALSE | FALSE | Y8 |  |  |  | 7 | [6 empty] | 25-08 | Xenta 401 | Xenta 491 | O_MSSB_B4
12 | 34 | TRUE | FALSE | K1 | FAN ENABLE | DO | 34K1 | 1 | To Be Advised | VFC by others | Volt free contact | _ | 0 | O-AHU-B432.1 | 12-08 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 34 | TRUE | FALSE | K2 | FAN ENABLE | DO | 34K2 | 2 | To Be Advised | VFC by others | Volt free contact | _ | 0 | O-AHU-B432.2 | 12-08 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 34 | TRUE | FALSE | K3 | FAN ENABLE | DO | 34K3 | 3 | To Be Advised | VFC by others | Volt free contact | _ | 0 | O-AHU-B432.3 | 12-08 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 34 | TRUE | FALSE | K4 | FAN ENABLE | DO | 34K4 | 4 | To Be Advised | VFC by others | Volt free contact | _ | 0 | O-AHU-B432.4 | 12-08 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 34 | TRUE | FALSE | K5 | FAN ENABLE | DO | 34K5 | 5 | To Be Advised | VFC by others | Volt free contact | _ | 0 | O-AHU-B423 | 12-08 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 34 | TRUE | FALSE | U1 | FAN STATUS | DI | 34U1 | 6 | 1Pair 7/0.20 Screen | VFC by others | Volt free contact | _ | 0 | O-AHU-B432.1 | 12-08 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 34 | TRUE | FALSE | U2 | FAN STATUS | DI | 34U2 | 7 | 1Pair 7/0.20 Screen | VFC by others | Volt free contact | _ | 0 | O-AHU-B432.2 | 12-08 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 34 | TRUE | FALSE | U3 | FAN STATUS | DI | 34U3 | 8 | 1Pair 7/0.20 Screen | VFC by others | Volt free contact | _ | 0 | O-AHU-B432.3 | 12-08 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 34 | TRUE | FALSE | U4 | FAN STATUS | DI | 34U4 | 9 | 1Pair 7/0.20 Screen | VFC by others | Volt free contact | _ | 0 | O-AHU-B432.4 | 12-08 | Xenta 401 | Xenta 421A | O_MSSB_B2
12 | 35 | TRUE | FALSE | Y1 | CHWV | AO | 35Y1 | 1 | 4Core 14/0.20 | M400 | Valve Actuator | TAC | 116 | O-AHU-B432.1 | 12-09 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 35 | TRUE | FALSE | Y2 | CHWV | AO | 35Y2 | 2 | 4Core 14/0.20 | M400 | Valve Actuator | TAC | 116 | O-AHU-B432.2 | 12-09 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 35 | TRUE | FALSE | Y3 | CHWV | AO | 35Y3 | 3 | 4Core 14/0.20 | M400 | Valve Actuator | TAC | 116 | O-AHU-B432.3 | 12-09 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 35 | TRUE | FALSE | Y4 | CHWV | AO | 35Y4 | 4 | 4Core 14/0.20 | M400 | Valve Actuator | TAC | 116 | O-AHU-B432.4 | 12-09 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 35 | TRUE | FALSE | Y5 | EDH SCR | AO | 35Y5 | 5 | 4Core 14/0.20 | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B432.1 | 12-09 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 35 | TRUE | FALSE | Y6 | EDH SCR | AO | 35Y6 | 6 | 4Core 14/0.20 | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B432.2 | 12-09 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 35 | TRUE | FALSE | Y7 | EDH SCR | AO | 35Y7 | 7 | 4Core 14/0.20 | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B432.3 | 12-09 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 35 | TRUE | FALSE | Y8 | EDH SCR | AO | 35Y8 | 8 | 4Core 14/0.20 | SCR | SCR Electric Heater | PCS | 50 | O-AHU-B432.4 | 12-09 | Xenta 401 | Xenta 491 | O_MSSB_B2
12 | 36 | TRUE | FALSE | U1 | SUPPLY AIR TEMP | AI | 36U1 | 1 | 1Pair 7/0.20 Screen | STD-100 150 | Duct Temperature | TAC | 0 | O-AHU-B432.1 | 12-10 | Xenta 401 | Xenta 451A | O_MSSB_B2
12 | 36 | TRUE | FALSE | U2 | SUPPLY AIR TEMP | AI | 36U2 | 2 | 1Pair 7/0.20 Screen | STD-100 150 | Duct Temperature | TAC | 0 | O-AHU-B432.2 | 12-10 | Xenta 401 | Xenta 451A | O_MSSB_B2
12 | 36 | TRUE | FALSE | U3 | SUPPLY AIR TEMP | AI | 36U3 | 3 | 1Pair 7/0.20 Screen | STD-100 150 | Duct Temperature | TAC | 0 | O-AHU-B432.3 | 12-10 | Xenta 401 | Xenta 451A | O_MSSB_B2
12 | 36 | TRUE | FALSE | U4 | SUPPLY AIR TEMP | AI | 36U4 | 4 | 1Pair 7/0.20 Screen | STD-100 150 | Duct Temperature | TAC | 0 | O-AHU-B432.4 | 12-10 | Xenta 401 | Xenta 451A | O_MSSB_B2
12 | 36 | TRUE | FALSE | U5 | ZONE TEMP | AI | 36U5 | 5 | 1Pair 7/0.20 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B432.1 | 12-10 | Xenta 401 | Xenta 451A | O_MSSB_B2
12 | 36 | TRUE | FALSE | U6 | ZONE TEMP | AI | 36U6 | 6 | 1Pair 7/0.20 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B432.2 | 12-10 | Xenta 401 | Xenta 451A | O_MSSB_B2
12 | 36 | TRUE | FALSE | U7 | ZONE TEMP | AI | 36U7 | 7 | 1Pair 7/0.20 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B432.3 | 12-10 | Xenta 401 | Xenta 451A | O_MSSB_B2
12 | 36 | TRUE | FALSE | U8 | ZONE TEMP | AI | 36U8 | 8 | 1Pair 7/0.20 Screen | STR100(1.8k,op) | Room Temperature | TAC | 13 | O-AHU-B432.4 | 12-10 | Xenta 401 | Xenta 451A | O_MSSB_B2
12 | 36 | FALSE | FALSE | Y1 |  |  |  | 9 | [6 empty] | 12-10 | Xenta 401 | Xenta 451A | O_MSSB_B2
12 | 36 | FALSE | FALSE | Y2 |  |  |  | 10 | [6 empty] | 12-10 | Xenta 401 | Xenta 451A | O_MSSB_B2